Camfil GlidePack MultiTrack 13 Specifications

1.0 General

1.1 - Filter housing shall be multi-stage air filter housing consisting of 16-gauge galvanized steel enclosure, multi-filter adaptable extruded aluminum filter mounting track, dual-access doors, three static pressure taps, door and filter gaskets and seals. In-line housing depth shall not exceed 13”.

1.2 - Sizes shall be as noted on enclosed drawings or other supporting materials.

2.0 Construction

2.1 - The housing shall be constructed of 16-gauge galvanized steel (stainless steel or aluminum*) with standing flanges to facilitate attachment to other HVAC system components. Corner posts of Z-channel construction shall ensure housing stability and rigidity. The housing shall be weatherproof and suitable for rooftop/outdoor installation without modification.

2.2 - The housing shall incorporate the capability of multiple stages of filtration without modification to the housing. A filter track, of extruded aluminum construction shall be an integral component of housing construction. The track shall accommodate 2”, or 4” deep prefilter, a 2”, or 4” deep intermediate particulate or carbon filter, or one 6” deep filter.

2.3 - Dual access swing-open doors shall include high-memory sponge neoprene gasket to facilitate a door-to-filter seal against all individual stages of filtration. Each door shall be equipped with adjustable and replaceable positive sealing UV-resistant star-style knobs and replaceable door hinges.

2.5 - The housing shall include three pneumatic fittings to allow the installation of static pressure gauge(s) to evaluate pressure drop across the prefilter, the secondary filter, the final filter, or any combination of the installed filters.

3.0 Performance

3.1 - Leakage at rated airflow, upstream to downstream of filter and slide mechanism shall not exceed 1% at 3.0” w.g. Leakage into or out of the housing shall be less than 1% at 3.0” w.g.

3.2 - Accuracy of pneumatic pressure fittings, when used to evaluate a single-stage, or multiple filter stages, shall be accurate within ± 3% at 0.6” w.g.

3.3 – Housing integrity to listed performance values shall be available on request from the housing manufacturer.

3.3 - Manufacturer shall provide evidence of facility certification to ISO 9001:2008.

Housings shall be Camfil GlidePack® MultiTrack 13 or approved equal.

* Items in parentheses may require selection.